**South Yorkshire Fire and Rescue**



**Barnsley District - Public Register of Notices Serviced – April 2021 to March 2023**

The Enforcement Register – This register details Enforcement, Prohibition and Alteration Notices that have been served on business premises under the [**Regulatory Reform (Fire Safety) Order 2005**](http://www.legislation.gov.uk/uksi/2005/1541/contents/made).

|  |  |
| --- | --- |
| Date on which notice served: | 21.12.2022 |
| Name and Address of Premises: | The Chicken Stop, 12 Market Street, Hoyland, Barnsley, S74 9QR. |
| Premises Type: | Other Sleeping Accommodation |
| Type of notice served: | Restriction |
| Details: | The Fire and Rescue Authority are further of the opinion that the matter(s) which **give rise** to the said risk **are:**  There is no fire resisting separation between the commercial kitchen and the means of escape from the upper floors. There is also no means of detecting a fire and giving warning to those sleeping on the upper floors.   |  | | --- | |  | |
| Reference No: | PN.NA.809 |
| Date of compliance of notice: |  |

|  |  |
| --- | --- |
| Date on which notice served: | 16.12.2022 |
| Name and Address of Premises: | Golden House, 208 Pontefract Road, Barnsley, S71 5QP. |
| Premises Type: | Other Sleeping Accommodation |
| Type of notice served: | Restriction |
| Details: | The Fire and Rescue Authority are further of the opinion that the matter(s) which **give rise** to the said risk **are:**   |  | | --- | | Inadequate means of protection for means of escape and Inadequate means of detection and warning | |
| Reference No: | PN.NA.808 |
| Date notice withdrawn. | **12.09.2023** |

|  |  |
| --- | --- |
| Date on which notice served: | 11.08.2022 |
| Name and Address of Premises: | Yummy House, 236 Midland Road, Royston, Barnsley, S71 4BP. |
| Premises Type: | Other Sleeping Accommodation |
| Type of notice served: | Restriction |
| Details: | The Fire and Rescue Authority are further of the opinion that the matter(s) which **give rise** to the said risk **are:**  Unsatisfactory means of escape from the upper floors.  Lack of fire alarm & detection system. |
| Reference No: | PN.NA.800 |
| Date of compliance of notice: | **26.09.2023** |

|  |  |
| --- | --- |
| Date on which notice served: | 04.08.2022 |
| Name and Address of Premises: | Scout Association, Silverwood Scout Camp, Barnsley Road, Silkstone, Barnsley, S75 4LE |
| Premises Type: | Other Sleeping Accommodation |
| Type of notice served: | Prohibition |
| Details: | The Fire and Rescue Authority are further of the opinion that the matter(s) which **give rise** to the said risk **is:**  Inadequate Means of Detection and Warning of Fire throughout the premises |
| Reference No: | PN.NA.797 |
| Date notice Withdrawn: | **10.11.2022** |

|  |  |
| --- | --- |
| Date on which notice served: | 04.08.2022 |
| Name and Address of Premises: | Scout Association, Silverwood Scout Camp, Barnsley Road, Silkstone, Barnsley, S75 4LE |
| Premises Type: | Other Premises open to Public |
| Type of notice served: | Prohibition |
| Details: | The Fire and Rescue Authority are further of the opinion that the matter(s) which **give rise** to the said risk **is:**  Inadequate means of detection and warning of fire throughout the premises |
| Reference No: | PN.NA.796 |
| Date notice Withdrawn: | **10.11.2022** |

|  |  |
| --- | --- |
| Date on which notice served: | 06.07.2022 |
| Name and Address of Premises: | CFTTB Barnsley & District Conservative Club, 36 Pitt Street, Barnsley, S70 1AW |
| Premises Type: | Social Club – Ancillary Sleeping Above |
| Type of notice served: | Enforcement |
| Details: | **Article 9 (1)**  The Fire Safety Risk Assessment was not suitable and sufficient  **Article 17 (1)**  The structural fire precautions are inadequately maintained  The manual fire fighting equipment is inadequately maintained  The fire alarm system is inadequately maintained  The emergency lighting is inadequately maintained  **Article 21 (2) (b)**  Safety training to employees is not repeated periodically |
| Reference No: | EN.NA.793 |
| Date of notice Withdrawn: | **23.09.2022** |

|  |  |
| --- | --- |
| Date on which notice served: | 17.06.2022 |
| Name and Address of Premises: | Royal Court Care Home, 22 Rock Mount, Hoyland, Barnsley, S74 9RP |
| Premises Type: | Care Home |
| Type of notice served: | Enforcement |
| Details: | **Article 9 (1)**  The Fire Safety Risk Assessment was not suitable and sufficient  **Article 14 (2) (b)**  The escape routes and exits could not be used as quickly and as safely as possible  **Article 17 (1)**  The passive fire precautions are inadequately maintained  **Article 21 (2) (a)**  Inadequate safety training is provided to enable the employees to safeguard themselves and other persons on the premises |
| Reference No: | EN.NA.785 |
| Date of compliance of notice: | **04.08.2022** |

|  |  |
| --- | --- |
| Date on which notice served: | 07.03.2022 |
| Name and Address of Premises: | Retrodome, Unit E, Upper New Street, Barnsley, S70 1LP. |
| Premises Type: | Amusement Arcade |
| Type of notice served: | Enforcement |
| Details: | **Article 9 (1)**  A Fire Safety Risk Assessment has not been carried out.  **Article 13 (1) (a) & 13 (2)**  The fire warning system is inadequate  **Article 14 (1)**  The escape routes were obstructed  **Article 14 (2) (b)**  The escape routes and exits could not be used as quickly and as safely as possible  **Article 14 (2) (h)**  The escape routes did not have adequate emergency lighting in case of failure of normal lighting circuits  **Article 15 (1) (a**)  Insufficient evacuation procedures and/or evacuation drills to be followed in the event of serious and imminent danger are in place  **Article 17 (1)**  The structural fire precautions are inadequately maintained  **Article 17 (1)**  The fire alarm system is inadequately maintained  **Article 17 (1**)  The emergency lighting is inadequately maintained  **Article 21 (1) (a)**  Inadequate safety training is provided to employees at the time when they are first employed  **Article 21 (2) (b)**  Safety training to employees is not repeated periodically |
| Reference No: | EN.NA.754 |
| Date of compliance of notice: | **11.05.2022** |

|  |  |
| --- | --- |
| Date on which notice served: | 17.02.2022 |
| Name of Organisation: | United Fried Chicken, 299 Barnsley Road, Cudworth, Barnsley, S72 8SY |
| Premises Type: | Ancillary Sleeping above Business Premises |
| Type of notice served: | Prohibition |
| Details: | The Fire and Rescue Authority are further of the opinion that the matter(s) which **give rise** to the said risk **is:**   |  | | --- | | Inadequate means of escape.  Inadequate means of protection to escape routes  Inadequate detection and warning | |
| Reference No: | PN.NA.735 |
| Date notice withdrawn: | **01.02.2024** |

|  |  |
| --- | --- |
| Date on which notice served: | 16.11.21 |
| Name of Organisation: | Mayfair Chinese Take Away, 6-8 Hoyland Road, Hoyland, Barnsley, S74 0LY |
| Premises Type: | Ancillary Sleeping above Business Premises |
| Type of notice served: | Enforcement |
| Details: | **Article 9 (1)**  A Fire Safety Risk Assessment has not been carried out  **Article 13 (1) (a) & 13 (2)**  The system is inadequate fire detection  **Article 13 (1) (a) & 13 (2)**  The fire warning system is inadequate  **Article 13 (1) (a) & 13 (2)**  The fire fighting equipment is inadequate  **Article 14 (2) (a)**  The escape routes did not lead, as directly as possible, to a place of safety  **Article 14 (2) (b)**  The escape routes and exits could not be used as quickly and as safely as possible  **Article 14 (2) (h)**  The escape routes were not adequately lit |
| Reference No: | EN.NA.722 |
| Date of compliance of notice: | **07.12.2021** |

|  |  |
| --- | --- |
| Date on which notice served: | 16.11.21 |
| Name of Organisation: | Mayfair Chinese Take Away, 6-8 Hoyland Road, Hoyland, Barnsley, S74 0LY |
| Premises Type: | Ancillary Sleeping above Business Premises |
| Type of notice served: | Prohibition |
| Details: | Insufficient means of escape  Insufficient measures in relation to the means for detecting fire and giving warning in case of fire. |
| Reference No: | PN.NA.723 |
| Date of compliance of notice: | **07.12.2021** |

|  |  |
| --- | --- |
| Date on which notice served: | 16.07.2021 |
| Name of Organisation: | Skyline Apartments, Heelis Street, Barnsley, S70 1LB |
| Premises Type: | Purpose Built Flats |
| Type of notice served: | Prohibition |
| Details: | **Article 13**  Provide sufficient means for detecting fire and giving warning |
| Reference No: | PN.NA.707 |
| Date of compliance of notice: | **26.08.2021** |

|  |  |
| --- | --- |
| Date on which notice served: | 22.07.2021 |
| Name of Organisation: | Skyline Apartments, Heelis Street, Barnsley, S70 1LB |
| Premises Type: | Purpose Built Flats |
| Type of notice served: | Enforcement |
| Details: | **Article 8 (1) (b)**  To take such general fire precautions as will ensure the safety of persons who are not his employees  **Article 9 (1)**  The Fire Safety Risk Assessment was not suitable and sufficient |
| Reference No: | EN.NA.708 |
| Date of compliance of notice: |  |